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KNX Presence Detector Manual

The manual refer to the following devices：

SATION-SS3001.1 PIR presence detector

SATION-SS3002.1 MW presence detector

SATION-SS3003.1 PIR presence detector with constant level light

SATION-SS3004.1 MW presence detector with constant level light

Zhuhai Sation Technology Co.Ltd
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Copyright Clarify

Copyright ownership belongs to Zhuhai Sation Technology Co.,Ltd. shall not be reproduced ,copied,or used in other ways without permission.Otherwise Zhuhai Sation Technology Co.Ltd will have the right to pursue legal responsibilities.

	
	
	Version

	Version NO.
	Release time
	
	Description

	
	
	
	

	V1.0
	Jan.30th.2016
	
	First release

	V1.1
	Sep.10th.2016
	
	Product update

	V1.2
	Dec.20th.2016
	
	Modify the technical parameters

	
	
	
	


Notice

1. Please carefully read this manual before using the product

2. This product is used in indoor environment and installed in electrical control box

3. Please install this product in a dry and ventilated place

4. Before power on, please confirm the input voltage according to the manual; after power on, please confirm the normal output voltage before connecting to the control bus

5. Please make sure the secure shell is in good condition, if the shell is damaged, please stop using to avoid accident

6. The power lead and ground lead must meet the requirement of Electrical Installation Standard

7. Only used indoor, model number need to be changed for outdoor use

8. This product is NOT a toy, please make sure it is out of childrens’ touch

9. Only be suitable for EIB/KNX system bus

10. Others:

The  below  sign  indicates  this  product  can’t  be  dealt  as  ordinary  family

rubbish,in order to avoid the possible environment and human health harm caused by the electrical waste, this product must follow recovery processing. Please contact the local recycling department after this product is scrapped, to make sure it can go as the right waste processing procedure.
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1 Technical data

KNX Bus Supply

AUX auxiliary power supply Supply current

consumption

Program button

LED Display

Detection range

Detection angle

Adjustable sensitivity level

Installation height

Installation

environment light Measurement range Temperature measurement range Operation temperature

Storage temperature Transport temperature



DC 21V~31V
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DC 12V~31V < 12mA <360mW
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Push shell cover or Fresenel lens to distribute physical address and program

LED
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High sensitivity area: 4~6m

Low sensitivity area:6~10m
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PIR:100°; MW:160° 10 level
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PIR :2m~4m, recommend:2.7m MW:2m~10m;

Celling
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1 lux~60k lux -20℃~55℃，±1.5℃ -5℃~+45℃ -25℃~+55℃ -30℃~+70℃
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2 Overview

2.1 Application Area

According to the brightness, Presence Detector via human body motion to control load automatically.realizing a comfortable, save energy, security purpose of intelligent building,It can be applied in many occasion, such as Office, Meeting room, Rest room, corridor, warehouse,staircase.etc.

2.2 Overview Functions

SATION Presence Detector functions are as follows:

1.Brightness detection range: 1 lux ~ 60k lux

2.Day/Night function can be configured independently and also can switching externally

3.Support motion monitor function of 3 kinds of output data. Such as switching value, dimming value, scene value.

4.Operating mode: manual mode; Full-automatic mode; semi-automatic mode; support stand by mode when input dimming.

5.Support setting work load brightness threshold. 6.Support motion detector from 0-10 level sensitivity. 7.Support setting work load cycle and idle cycle.

8.Support master-slave function. Master have 3 kinds of output data. 9.Support brightness value output , the value can be send in circle mode at

scheduled time.

10.Support the changing brightness value output to toggle to switching mode.

11.Support correct brightness value via external or internal. 12.Support constant level light function.

13.Support measured temperature value cycle send.
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